SECTION 13 05 41
SEISMIC RESTRAINT REQUIREMENTS FOR NON-STRUCTURAL COMPONENTS

PART 1 – GENERAL

1.1 DESCRIPTION:

A.	Provide seismic restraint in accordance with the requirements of this section in order to maintain the integrity of nonstructural components of the building so that they remain safe and functional in case of seismic event.

B.	Definitions: Non-structural building components are components or systems that are not part of the building’s structural system whether inside or outside, above or below grade. Non-structural components of buildings include:

1.	Architectural Elements: Facades that are not part of the structural system and its shear resistant elements; cornices and other architectural projections and parapets that do not function structurally; glazing; nonbearing partitions; suspended ceilings; stairs isolated from the basic structure; cabinets; bookshelves; medical equipment; and storage racks.

2.	Electrical Elements: Power and lighting systems; substations; switchgear and switchboards; auxiliary engine-generator sets; transfer switches; motor control centers; motor generators; selector and controller panels; fire protection and alarm systems; special life support systems; and telephone and communication systems.

3.	Mechanical Elements: Heating, ventilating, and air-conditioning systems; medical gas systems; plumbing systems; sprinkler systems; pneumatic systems; boiler equipment and components.

4.	Transportation Elements: Mechanical, electrical and structural elements for transport systems, i.e., elevators and dumbwaiters, including hoisting equipment and counterweights.

1.2 QUALITY CONTROL:

A.	Shop-Drawing Preparation:

1.	Have seismic-force-restraint shop drawings and calculations prepared by a professional structural engineer experienced in the area of seismic force restraints. The professional structural engineer shall be registered in the state where the project is located.

2.	Submit design tables and information used for the design-force levels, stamped and signed by a professional structural engineer registered in the State where project is located.

B.	Coordination:

1.	Do not install seismic restraints until seismic restraint submittals are approved by the COTR.

2.	Coordinate and install trapezes or other multi-pipe hanger systems prior to pipe installation.

1.4 SUBMITTALS:

A.	Submit a coordinated set of equipment anchorage drawings prior to installation including:

1.	Description, layout, and location of items to be anchored or braced with anchorage or brace points noted and dimensioned.

2.	Details of anchorage or bracing at large scale with all members, parts brackets shown, together with all connections, bolts, welds etc. clearly identified and specified.

3.	Numerical value of design seismic brace loads.

4.	For expansion bolts, include design load and capacity if different from those specified.

B.	Submit prior to installation, a coordinated set of bracing drawings for seismic protection of piping, with data identifying the various support-to-structure connections and seismic bracing structural connections, include:

1.	Single-line piping diagrams.

2.	Type of pipe (Copper, steel, cast iron, insulated, non-insulated, etc.).

3.	Pipe contents.

4.	Structural framing.

5.	Location of all gravity load pipe supports and spacing requirements.

6.	Numerical value of gravity load reactions.

7.	Location of all seismic bracing.

8.	Numerical value of applied seismic brace loads.

9.	Type of connection (Vertical support, vertical support with seismic brace etc.).

10.	Seismic brace reaction type (tension or compression). Details illustrating all support and bracing components, methods of connections, and specific anchors to be used.

C.	Submit prior to installation, bracing drawings for seismic protection of suspended ductwork and suspended electrical and communication cables, include:

1.	Details illustrating all support and bracing components, methods of connection, and specific anchors to be used.

2.	Numerical value of applied gravity and seismic loads and seismic loads acting on support and bracing components.

3.	Maximum spacing of hangers and bracing.

4.	Seal of registered structural engineer responsible for design.

D.	Submit design calculations prepared and sealed by the registered structural engineer specified above in paragraph 1.3A.

E.	Submit for concrete anchors, the appropriate ICBC evaluation reports, OSHPD pre-approvals, or lab test reports verifying compliance with OSHPD Interpretation of Regulations 28-6.

1.5 APPLICABLE PUBLICATIONS:

A.	The Publications listed below (including amendments, addenda revisions, supplements and errata) form a part of this specification to the extent referenced. The publications are referenced in text by basic designation only.

B.	American Concrete Institute (ACI):

355.2-07	Qualification for Post-Installed Mechanical Anchors in Concrete and Commentary

C.	American Institute of Steel Construction (AISC):

Load and Resistance Factor Design, Volume 1, Second Edition.

D.	American Society for Testing and Materials (ASTM):

A36/A36M-05	Standard Specification for Carbon Structural Steel.

A53/A53M-07	Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

A307 (REV A-07)	Standard Specification for Carbon Steel Bolts and Studs; 60,000 PSI Tensile Strength.

A325-07	Standard Specification for Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength.

A325M-05	Standard Specification for High-Strength Bolts for Structural Steel Joints [Metric].

A490-06	Standard Specification for Heat-Treated Steel Structural Bolts, 150 ksi Minimum Tensile Strength.

A490M (REV A-04)	Standard Specification for High-Strength Steel Bolts, Classes 10.9 and 10.9.3, for Structural Steel Joints [Metric].

A500/A500M-07	Standard Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes.

A501-07	Specification for Hot-Formed Welded and Seamless Carbon Steel Structural Tubing.

A615/A615M-07	Standard Specification for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement.

A992/A992M (REV A-06)	Standard Specification for Steel for Structural Shapes for Use in Building Framing.

A996/A996M (REV A-06)	Standard Specification for Rail-Steel and Axel-Steel Deformed Bars for Concrete Reinforcement.

E488-96(R2003)	Standard Test Method for Strength of Anchors in Concrete and Masonry Elements.

E.	International Building Code (IBC) 2003 Edition.

F.	VA Seismic Design Requirements, H-18-8, December 2003.

G.	National Uniform Seismic Installation Guidelines (NUSIG).

H.	Sheet Metal and Air Conditioning Contractors National Association (SMACNA):

Seismic Restraint Manual - Guidelines for Mechanical Systems, 1998 	Edition and Addendum.

1.6 Regulatory Requirement:

A.	IBC 2003.

B.	Exceptions: The seismic restraint of the following items may be omitted:

1.	Equipment weighing less than 400 pounds, which is supported directly on the floor or roof.

2.	Equipment weighing less than 20 pounds, which is suspended from the roof or floor or hung from a wall.

3.	Gas and medical piping less than 2 ½ inches inside diameter.

4.	Piping in boiler plants and equipment rooms less than 1 ¼ inches inside diameter.

5.	All other piping less than 2 ½ inches inside diameter, except for automatic fire suppression systems.

6.	All piping suspended by individual hangers, 12 inches or less in length from the top of pipe to the bottom of the support for the hanger.

7.	All electrical conduits, less than 2 ½ inches inside diameter.

8.	 All rectangular air handling ducts less than six square feet in cross sectional area.

9.	All round air handling ducts less than 28 inches in diameter.

10.	All ducts suspended by hangers 12 inches or less in length from the top of the duct to the bottom of support for the hanger.

PART 2 – PRODUCTS

2.1 STEEL:

A.	Structural Steel: ASTM A992.

B.	Structural Tubing: ASTM A500, Grade B.

C.	Steel Pipe: ASTM A53/A53M, Grade B.

D.	Bolts & Nuts: ASTM A307.

2.2 CAST-IN-PLACE CONCRETE:

A.	Concrete: 28 day strength, f’c = 25 MPa (3,000 psi).

B.	Reinforcing Steel: ASTM A-706 Grade 60.

PART 3 – EXECUTION

3.1 CONSTRUCTION, GENERAL:

A.	Provide equipment supports and anchoring devices to withstand the seismic design forces, so that when seismic design forces are applied, the equipment cannot displace, overturn, or become inoperable.

B.	Provide anchorages in conformance with recommendations of the equipment manufacturer and as shown on approved shop drawings and calculations.

C.	Construct seismic restraints and anchorage to allow for thermal expansion.

D.	Testing Before Final Inspection:

1.	Test 10-percent of anchors in masonry and concrete per ASTM E488, and ACI 355.2 to determine that they meet the required load capacity. If any anchor fails to meet the required load, test the next 20 consecutive anchors, which are required to have zero failure, before resuming the 10-percent testing frequency.

2.	Before scheduling Final Inspection, submit a report on this testing indicating the number and location of testing, and what anchor-loads were obtained.

3.2 EQUIPMENT RESTRAINT AND BRACING:

A.	See drawings for equipment to be restrained or braced.

3.3 MECHANICAL DUCTWORK and piping; boiler plant stacks and breaching; electrical busways, conduits, and cable trays; and telecommunication wires and cable trays

A.	Support and brace mechanical ductwork and piping; electrical busways, conduits and cable trays; and telecommunication wires and cable trays including boiler plant stacks and breeching to resist directional forces (lateral, longitudinal and vertical).

B.	Brace duct and breeching branches with a minimum of 1 brace per branch.

D.	Provide supports and anchoring so that, upon application of seismic forces, piping remains fully connected as operable systems which will not displace sufficiently to damage adjacent or connecting equipment, or building members.

E.	Seismic Restraint of Piping:

1.	Design criteria:

a.	Piping resiliently supported: Restrain to support 120 -percent of the weight of the systems and components and contents.

b.	Piping not resiliently supported: Restrain to support 60 -percent of the weight of the system components and contents.

F.	Piping Connections: Provide flexible connections where pipes connect to equipment. Make the connections capable of accommodating relative differential movements between the pipe and equipment under conditions of earthquake shaking.

- - - E N D - - -